Urgent Demonstration Project for Next-Generation Bi-directional Communication Output Control

Inverter with power control function

(less than 6 6 k V)

Schedule Information Distribution System Transmission Specification (Power Plant)

2015.08.25		Establishment

2015.12.10				Revision

KYUSHU ELECTRIC POWER CO., INC

Prohibition of Use, Reproduction, and Disclosure Other Than Purpose

| Change Further Notes Record REVISIONS |  |  |
| --- | --- | --- |
| Change symbol REV. MARK Change Issue Date REV. ISSU ED | Paged PAGE | CHANGED PLACE AND CONTENTS |
| 0 |  | First edition published |
|  | 6 | Table 2 . 1 Add Cipher Suite |
|  | 15 | 3 . 3 Change the description of the header section from the number of records to the number of data |
| 1 | 16 17 | 3 . 3 . 1 "0 00 0" is added to the explanation of "Control date and time" of the transmission field. 3 . 3 . 2 "0 00 0" is added to the explanation of "Control date and time" of the transmission field. |
| 15.10.09 | 21 22 | 4 . 2 . 2 Changes the output of error messages. 4 . 2 . 3 Add (Re-assign page number thereafter) |
|  | 7 | Table 2 . 2 Describe URL |
|  | 8 | Figure 2. 2 Changing Examples of Requests to U R L |
|  | 20 | Table 4 . 1 Change HT T P status code " 4 x x" to "Not required" for retry. |
| 2 | 21 | 4 . 2 . 1 Added a description of the file name of the error file. |
|  | 21 | 4 . 2 . 2 Changed supplementary explanation of error file. |
| 15.10.23 | 22 | Table 4 . 4 Delete error messages that you do not want to deliver |
|  | 23 | Table 5 . 2 Describe FQDN |
|  | 9 | Transmit example response file (Figure 2). 3) and the error file (Figure 2. To 4) and the contents of the description |
|  |  | Review |
|  | 13 | 3 . 3 With a file format of 3. 2 Change to file format (page numbering again) |
|  |  | Figure 3. 2 Figure 3 shows an example of the transmission file format. 1 Change to transmission file format example |
|  |  | Figure 3. 1 The format of the data section is "*3. Changed to "See Chapter 4" |
|  | 14 | 3 . 2 With binary conversion rules 3. 3 Change to binary conversion rule |
| 3 |  | Figure 3. 1 Example of binarization (data part) is shown in Figure 3. 2 Changed to binary example Figure 3. The example of binary conversion of the header part is described in 2. |
| 15.11.06 | 15 | Figure 3. Change the number of data items in 2 to the number of output control rate data items. 3 . 4 Added data part format (Chapters numbering again) |
|  |  | 3 . 4 . 1 Change the explanation of the transmission item "Control date and hour" to "DD hh mm is "0 10 00"... |
|  |  | 3 . 4 . 1 Change the transmission item name to "Number of output control rate data" |
|  | 16 | 3 . 4 . 2 Change the explanation of the transmission item "Control date and hour" to "DD hh mm is "0 10 00"... |
|  |  | 3 . 4 . 2 Change the transmission item name to "Number of output control rate data" |
|  | 17 | 3 . 4 . 3 Change the transmission item name to "Number of output control rate data" |
| 4 | 9 | Figure 2. 3 Removed " ch ar se t= UT F 8 " from HT T P response header and HT T P response body. Modified fi le na m e. Figure 2. 4 Removed " ch ar se t= UT F 8 " from HT T P response header Figure 2. 4 Changing HT T P response body to "Co nt en t-Ty pe : tex t/p la in" |
| 15.11.13 | 10 |  |
| 5 15.12.10 | 2 0 | Add variable length to error message data type |

Table of Contents

1 SUMMARY	3

1.1 Purpose	3

1.2 Range of this document	3

1.3 Definition of Terms	4

2 Data linkage.	6

2.1 Communication Overview	6

2.2 Outline of the linkage	7

2.3 Request timing	12

2.3.1 Fixed schedule (annual) and fixed schedule (monthly) requirements	12

2.3.2 Requesting an Update Schedule	12

2.3.3 Request for ID registration confirmation	12

3 Transmission file	13

3.1 File Formats and Naming Conventions	13

3.2 File formats	13

3.3 Binary conversion rules	14

3.4 Format of the data section	15

3.4.1 Fixed schedule (annual)	15

3.4.2 Fixed schedule (monthly)	16

3.4.3 Update schedule	17

3.4.4 ID registration confirmation result	18

4 Linkage error.	19

4.1 Response error	19

4.2 Application error	20

4.2.1 File Formats and Naming Conventions	20

4.2.2 File formats	20

4.2.3 Error Message	21

5 Time synchronization.	22

5.1 Overview of time synchronization	22

5.2 Time Synchronization Protocol	22

5.3 Time Synchronization Timing	23

Figure 1.1 Scope of this Manual	3

Figure 1.2 Power Station ID	4

Figure 2.1 Overview of Communications	6

Figure 2.2 Example request	8

Figure 2.3 Example response (transmission file)	9

Figure 2.4 Example response (error file)	10

Figure 3.1 Format configuration of transmission file	13

Figure 3.2 Example of binarization	14

Figure 5.1 Overview of Time Synchronization	22

Table 2.1 Overview of communication	6

Table 2.2 Request URL	7

Table 2.3 Request parameters	7

Table 2.4 Schedule categories	7

Table 2.5 Outline of transmission files	10

Table 2.6 Schedule categories and transmission files	11

Table 2.7 Request timing for fixed schedules	12

Table 4. 1 HTTP status codes	19

Table 4.2 Retry timing when a response error occurs	19

Table 4.3 Error code system	21

Table 4.4 List of error messages	21

Table 5.1 Communication Specifications for Time Synchronization	22

Table 5. 2 NTP Server Settings	22

Table 5.3 Time Synchronization Timing	23

Table 5.4 Periodic update timing	23

1 SUMMARY

1.1 Purpose

This document describes how to link schedule information distribution systems, such as schedule information, to power plants.

1.2 Range of this document

The scope of this document is shown in Figure 1.1.

Schedule information distribution system

Distributor

Power plant

Power plant

: Scope of this document

Figure 1.1 Scope of this Manual

1.3 Definition of Terms

Major terms in this document are defined below.

- Power plant ID

ID consisting of 26 digits of the receiving point identification number (22 digits) + branch number (3 digits) + checksum (1 digit). Figure 1.2 shows the configuration of the high-and low-pressure power plant ID.

|  | High and low pressure division |  | Each power-specific code |  | Branch number |  | Checksum |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | (1 digit) |  | (19 digits) |  | (3 digits) |  | (1 digit) |
| + | ▲ | + | ■■■・・・■■■ | + | ○○○ | + | □ |

●●

Power Transmission and Distribution Operator Code

(2 digits)

Equivalent to receiving point identification number (22 digits)

Figure 1.2 Power Station ID

- Checksum

A checksum shall be provided for the plant ID and schedule in order to detect input errors and prevent data tampering.

The following shows how to calculate the checksum for each data item.

(a) Power plant ID

(1st digit × 1) + (3rd digit × 5) + (5th digit × 9) + (6th digit × 1) + (7th digit × 5) + (9th digit × 9) + (11th digit × 3) + (13th digit × 5) + (14th digit × 9) + (16th digit × 1) + (17th digit × 3) + (18th digit × 5) + (9th digit × 7) + (20th digit × 9))

(21st digit × 1) + (22nd digit × 3) + (23rd digit × 5) + (24th digit × 7) + (25th digit × 9)

The checksum of the plant ID shall be the last digit of the solution obtained by the following formula.

Example) When power plant ID (excluding checksum part) is 1234567890123456789012345 (1 × 1) + (2 × 3) + (3 × 5) + (4 × 7) + (5 × 9) +

(6×1)+(7×3)+(8×5)+(9×7)+(0×9)+

(1×1)+(2×3)+(3×5)+(4×7)+(5×9)+

(6×1)+(7×3)+(8×5)+(9×7)+(0×9)+

(1×1)+(2×3)+(3×5)+(4×7)+(5×9)=545

The checksum is the last digit "5" of the solution.

(b) Fixed schedule and update schedule

The checksum of the fixed schedule and the update schedule shall be the last two digits of the solution obtained by the following formula.

(Output control rate 1 + Output control rate 2 + Output control rate 3...)

Divided by (month, month, and hour of control + day, month, and hour of control)

Example: Output Control Rate 1:100	Output control ratio 2:40	Output Control Rate 3:28 Date/Time of Control: 201503271005

(100+40+28) ÷(3+27) = 5 Remaining 18 checksum is the remainder "18".

2 Data linkage

2.1 Communication Overview

The communication between the plant and the scheduling information delivery system uses HTTPS(Hyper Text Transfer Protocol Secure) to communicate via secure communication provided by Transport Layer Security (TLS) protocol (see Fig. 2.1). This secure communication prevents eavesdropping, tampering, and spoofing of data.

In order to perform this HTTPS communication, a root certificate is allocated to the plant (client), and a server certificate issued by a certificate authority is allocated to the scheduling information distribution system (server). These certificates are used to authenticate HTTPS communication.

Schedule information distribution system

Power plant

①

HTTPS-REQUEST

Table 2.1 shows the outline of HTTPS communication.

②

HTTPS-RESPONSE

Figure 2.1 Overview of Communications

Table 2.1 Communication Summary

| Communication method | HTTPS(Hyper Text Transfer Protocol Secure) |
| --- | --- |
| Communications protocols | TLS(Transport Layer Security)1.2 |
|  | HTTP(Hypertext Transfer Protocol)1.1 |
| Cipher suite | TLS_RSA_WITH_AES_128_CBC_SHA256 TLS_RSA_WITH_AES_256_CBC_SHA256 |

2.2 Outline of the linkage

- Requirements from power plants (HTTPS-REQUEST)

The plant requests files such as schedules to the scheduling information distribution system for the URLs and ports shown in Table 2.2.

Table 2.2 Request URL

| Scheduling information distribution server | URL | https://re-ene.kyuden.co.jp/scheduleSend/ |
| --- | --- | --- |
|  | Port | 443 |

In addition, requests for files are made to the scheduling information distribution system using POST(METHOD attributes). Table 2.3 shows the parameters when requesting a file.

Table 2.3 Request parameters

| Logical name | Physical name | Data type | Description |
| --- | --- | --- | --- |
| Power plant ID | Power_plant_id | 26 digits of the string | - |
| MAC address | Mac_address | 12-digit string | Only hexadecimal values excluding the conjunctions ":", "-", etc. shall be used, and alphabetic characters shall be uppercase. e.g., "01-23-89-ab-cd-ef" 「012389ABCDEF」 |
| Schedule classification | Schedule_kbn | 4-digit string | See Table 2.4 |

Table 2.4 shows the schedule categories for the request parameters.

Table 2.4 Schedule categories

| Category value | Description |  |
| --- | --- | --- |
| 999_ | Fixed schedule (annual) | The last digit <_> is an item in the update schedule file. Specify the fixed schedule update flag, Specifies which fixed schedule (annual) you want to acquire. |
| YYMM | For the 20YY MM month Fixed schedule (monthly) | When acquiring a fixed schedule (month and year), specify the year and month. |
| 0000 | Update schedule | - |
| 8888 | For ID registration confirmation | Confirm whether or not the power station ID is registered. |

Figure 2.2 shows an example of the minimum requests required to request a file.

POST /scheduleSend/ HTTP/1.1

Host: re-ene.kyuden.co.jp Connection: close Content-Length: 107 Content-type: application/x-www-form-urlencoded ・ ・ ・

(Empty lines)

Power_plant_id=23498213471000000000000017&mac_address=012389ABCDEF &schedule_kbn=0000

HTTP request

HTTP header

HTTP body

Figure 2.2 Example request

POST

Keep-Alive Off

See Table 2.3

- Reply from Scheduled Information Delivery System (HTTPS-RESPONSE)

The schedule information distribution system responds to the power plant with the file based on the schedule segment requested by the power plant.

A response to a file returns a multipart response (Content-Type: multipart/mixed).

Figure 2.3 shows an example response (transmission file) and Figure 2.4 shows an example response (error file).

HTTP Response Status

HTTP response headers

HTTP response body

HTTP/1.1 200 OK

Content-Type: multipart/mixed;boundary="BOUNDARY" Content-Length: 19970 Connection: close ・ ・ ・

(Empty lines)

-- BOUNDARY

Content-Length: 19729 Content-Type: application/octet-stream Content-Disposition: attachment; filename=201_9990_123456789012345 67890123456_20150831123059.data ・ ・ ・

(Empty lines)

Transmission file (binary file) ※ See chapter 3

-- BOUNDARY--

Figure 2.3 Example response (transmission file)

Delimiter

Download file

Delimiter

HTTP Response Status

HTTP response headers

HTTP response body

HTTP/1.1 200 OK

Content-Type: multipart/mixed;boundary="BOUNDARY" Content-Length: 262 Connection: close ・ ・ ・

(Empty lines)

-- BOUNDARY

Content-Length: 239 Content-Type: text/plain; charset=UTF-8 Content-Disposition: attachment; filename=ERR_0000_123456789012345 67890123456_20150831123059.data ・ ・ ・

(Empty lines)

Error file (text file) ※ See chapter 4.2

-- BOUNDARY--

Figure 2.4 Example response (error file)

Delimiter

Download file

Delimiter

| Transmission file | Description | Format № |
| --- | --- | --- |
| Fixed schedule (annual) | Annual fixed schedule information | 201 |
| Fixed schedule (monthly) | Fixed schedule information for the month | 202 |
| Update schedule | Update schedule information | 203 |
| ID registration confirmation result | Information on the registration confirmation result of the power station ID | 301 |

A summary of the file is shown in Table 2.5. A description of the file format is given in Section 3.4. Table 2.5 Outline of transmission files

The transmission file responsive to the plant for the requested schedule segment is shown in Table 2.6.

Table 2.6 Schedule categories and transmission files

| Transmission file Schedule classification |  | Fixed schedule (annual) | Fixed schedule (monthly) | Update schedule | ID registration confirmation result |
| --- | --- | --- | --- | --- | --- |
|  |  | 201 | 202 | 203 | 301 |
| 999_ | Fixed schedule (annual) | ○ |  |  |  |
| YYMM | Fixed schedule (monthly) |  | ○ |  |  |
| 0000 | Update schedule |  |  | ○ |  |
| 8888 | Confirmation of ID registration |  |  |  | ○ |

2.3 Request timing

2.3.1 Fixed schedule (annual) and fixed schedule (monthly) requirements

When the Fixed Schedule Update Flag item in the update schedule file is changed, a request is made to the schedule information delivery system for the fixed schedule (yearly) or fixed schedule (monthly) delivery.

The request to the schedule information distribution system is made in a time zone in which the request can be made to prevent the request from the distribution business operator or the power station from concentrating, and the load distribution is attempted. Therefore, when a request is made from a power station, the request shall be made in the time zone shown in Table 2.7 according to the value of the checksum at the end of the power station ID.

Table 2.7 Request timing for fixed schedules

| Checksum | Required time zone |
| --- | --- |
| 0 | 21:10:00 ～ 21:29:59 |
| 1 | 21:40:00 ～ 21:59:59 |
| 2 | 22:10:00 ～ 22:29:59 |
| 3 | 22:40:00 ～ 22:59:59 |
| 4 | 23:10:00 ～ 23:29:59 |
| 5 | 23:40:00 ～ 23:59:59 |
| 6 | 0:10:00 ～ 0:29:59 |
| 7 | 0:40:00 ～ 0:59:59 |
| 8 | 1:10:00 ～ 1:29:59 |
| 9 | 1:40:00 ～ 1:59:59 |

2.3.2 Requesting an Update Schedule

Requests for update schedules from the plant shall be made at the time specified in the item "Next Access Date" of the update schedule file.

2.3.3 Request for ID registration confirmation

For the ID registration confirmation, after receiving the power station ID or replacing the equipment, the power station makes a request as necessary.

3 Transmission file

The format of the transmission file that the scheduling information distribution system responds to requests from the plant is shown below.

3.1 File Formats and Naming Conventions

The format and file name of the file transmitted from the schedule information distribution system shall be as follows.

① Format: Binary file

② Character code :UTF-8

③ Byte Order: Network Byte Order

④ Filename: data of CCC_FFFF_XXXXXXXXXXXXXXXXXXXXXXXXXX_YYYYMMDDhhmmss.

CCC: Format No (without zero suppression)	※ Refer to Table 2.5 FFFF: Requested scheduling classification (without zero suppression) * Refer to Table 2.4 XXXXXXXXXXXXXXXXXXXXXXXXXX: Power plant ID

YYYY	: MM of the date and time of file generation in the schedule information delivery system	:	〃	Month

DD	:	〃	Day

Hh	:	〃	Time

Mm	:	〃	Minutes

Ss	:	〃	Second

e.g. Fixed schedule for request from plant ID 12345678901234567890123456

(Yearly) (Formatted No201) When a response file is generated at 10:5:20 on May 5, 2015

201_9990_12345678901234567890123456_20150505100520.data

3.2 File formats

The transmission file consists of a header section and a data section. The header portion outputs the number of data of the data portion, the data portion repeatedly outputs each format by the number of data of the header portion.

Figure 3.1 shows the format structure of the transmission file.

Data section

(Repeat same format)

Header (6byte)

| Format No:XXX | Format No:XXX | Format No:XXX |
| --- | --- | --- |

Number of data

Repeat the number of data items in the header section.

(See Chapter 3.4)

Figure 3.1 Format configuration of transmission file

3.3 Binary conversion rules

The schedule information distribution system creates a binary format file as a transmission file to respond according to the following rules.

  - Binary conversion of the header section and data section is performed in hexadecimal (1 byte) in 1-digit units. However, the output control rate is binary converted in hexadecimal (1 byte) for each data.

  - The basic fixed length shall be defined. However, the portion of the output control rate is a variable length, and the number of bytes is represented by the number of output control rate data.

Figure 3.2 shows an example of a binary update schedule.

Figure 3.2 Example of binarization

3.4 Format of the data section

The format of the data portion of the transmission file is shown below.

3.4.1 Fixed schedule (annual)

This property indicates the fixed schedule (annual) format.

[Format No. 201]

| Item | In bytes | Explanation |
| --- | --- | --- |
| Schedule ID | 10Byte | - |
| Power plant ID | 26Byte | - |
| Date and time of control | 12Byte | Sets the year, month, day, hour, and minute of the first schedule frame. Formatting: YYYYMMDDhhmm ※ DDhhmm is "010000" |
| Number of output control rate data | 5Byte | Number of output control rate data (maximum 1488) ※ Up to 1488 for the maximum number of days of the relevant month separated by 30 minutes (24 hours/0.5 hours × 31 days) |
| Output control rate | 1Byte x number of data | Unit: % Repeat for the number of output control rate data (maximum 1488) |
| Checksum | 2Byte | - |

(Supplementary explanations)

The fixed schedule of the requested power plant for 13 months is output. The image of the file at this time is shown below.

At the power plant that made the request

Fixed schedule of 13 months

| Schedule ID... checksum | ・・・ | Schedule ID... checksum |
| --- | --- | --- |

| Schedule ID | Power plant ID | Date and time of control | Number of output control rate data | Output control rate | Checksum |
| --- | --- | --- | --- | --- | --- |

| Output control rate 1 | Output control rate 2 | ・・・ | Output control rate N |
| --- | --- | --- | --- |

N: Number of output control rate data

3.4.2 Fixed schedule (monthly)

This property indicates the format of a fixed schedule (monthly).

[Format No. 202]

| Item | In bytes | Explanation |
| --- | --- | --- |
| Schedule ID | 10Byte | - |
| Power plant ID | 26Byte | - |
| Date and time of control | 12Byte | Sets the year, month, day, hour, and minute of the first schedule frame. Formatting: YYYYMMDDhhmm ※ DDhhmm is "010000" |
| Number of output control rate data | 5Byte | Number of output control rate data (maximum 1488) ※ Up to 1488 for the maximum number of days of the relevant month separated by 30 minutes (24 hours/0.5 hours × 31 days) |
| Output control rate | 1Byte x number of data | Unit: % Repeat for the number of output control rate data (maximum 1488) |
| Checksum | 2Byte | - |

(Supplementary explanations)

Output information for one month of the fixed schedule of the power plant that made the request. The image of the file at this time is shown below.

One month's fixed schedule for the power plant that made the request

Schedule ID... checksum

| Schedule ID | Power plant ID | Date and time of control | Number of output control rate data | Output control rate | Checksum |
| --- | --- | --- | --- | --- | --- |

| Output control rate 1 | Output control rate 2 | ・・・ | Output control rate N |
| --- | --- | --- | --- |

N: Number of output control rate data

3.4.3 Update schedule

Indicates the format of the update schedule.

[Format No. 203]

| Item | In bytes | Explanation |
| --- | --- | --- |
| Schedule ID | 10Byte | - |
| Power plant ID | 26Byte | - |
| Date and time of control | 12Byte | Sets the year, month, day, hour, and minute of the first schedule frame. Formatting: YYYYMMDDhhmm |
| Number of output control rate data | 5Byte | Number of output control rate data (maximum 336) ※ A maximum of 336 is the maximum number of update days separated by 30 minutes. (24 hours/0.5 hours × 7 days) |
| Output control rate | 1Byte x number of data | Unit: % Repeat for the number of output control rate data (maximum 336) |
| Fixed Schedule Update Flag | 1Byte | Count up when fixed schedule is updated, and new fixed schedule can be acquired. Flag that notifies you of the fact. |
| Checksum | 2Byte | - |
| Next access date and time | 14Byte | Set the next delivery date and time. Formatting: YYYYMMDDhhmmss |

(Supplementary explanations)

The information on the update schedule of the requested power station is output for up to seven days. The image of the file at this time is shown below.

Schedule ID... Next access date and time

Schedule for renewal of the plant that made the request

| Schedule ID | Power plant ID | Date and time of control | Output control rate Number of data | Output Control rate | Fixed schedule Update flag | Checksum | Next time Access date and time |
| --- | --- | --- | --- | --- | --- | --- | --- |

| Output control rate 1 | Output control rate 2 | ・・・ | Output control rate N |
| --- | --- | --- | --- |

N: Number of output control rate data

3.4.4 ID registration confirmation result

The format of the registration confirmation result of the power station is shown.

[Format No. 301]

| Item | In bytes | Explanation |
| --- | --- | --- |
| Power plant ID | 26Byte | - |
| Results of registration confirmation | 1Byte | 0: ID registered 1: ID not registered |

(Supplementary explanations)

One registration confirmation result of the requested power station is output. You respond with a single file.

The image of the file at this time is shown below.

Results of registration confirmation

Power plant ID

4 Linkage error

In addition to the mere communication error between the power station and the schedule information distribution system, "response error" and "application error" exist as request time errors from the power station to the schedule information distribution system. These two are shown below.

4.1 Response error

| Http status code | Meaning of the response | Necessity of retry |
| --- | --- | --- |
| 1xx | Information | Required |
| 2xx | Success | Unnecessary |
| 3xx | Redirection | Required |
| 4xx | Client error | Unnecessary |
| 5xx | Server error | Required |

Response errors are identified by a HTTP status code. HTTP status code is shown in Table 4.1. Table 4. 1 HTTP status codes

Table 4.2 shows the retry timing when HTTP status code is other than "2xx". Provided, however, that any error at the time of manual request at the time of initial installation, etc. shall be retried at any time.

Table 4.2 Retry timing when a response error occurs

| Schedule classification |  | Timing | Retry Number of times | During a retry error Retry timing |
| --- | --- | --- | --- | --- |
| 999_ | Fixed schedule (annual) | Retry after 5 minutes | 5 times | Designated time zone for the following day |
| YYMM | Fixed schedule (monthly) | 〃 |  | 〃 |
| 0000 | Update schedule | 30 minutes after the next access date and time |  | Continue retry after 30 minutes |
| 8888 | Confirmation of ID registration | Retry at any time | - | - |

4.2 Application error

If there is no error in the request information or information on the request, an error file is returned as a file. The power station shall respond to the contents notified in the error file and perform a retry.

4.2.1 File Formats and Naming Conventions

The format and file name of the error file transmitted from the schedule information distribution system are as follows.

① Format: Text file

② Character code :UTF-8

③ Line feed: None

④ Filename: data of ERR_FFFF_XXXXXXXXXXXXXXXXXXXXXXXXXX_YYYYMMDDhhmmss.

FFFF: Schedule division requested (zero-padding, top four digits if request is five digits or more)

※ See Table 2.4

XXXXXXXXXXXXXXXXXXXXXXXXXX: plant ID (zero-padding, leading 26 digits if the requirement is 27 digits or more)

YYYY: Year of the file generation date and time in the scheduled information delivery system

| MM | : | 〃 | Month |
| --- | --- | --- | --- |
| DD | : | 〃 | Day |
| Hh | : | 〃 | Time |
| Mm | : | 〃 | Minutes |
| Ss | : | 〃 | Second |

e.g. Fixed schedule for request from plant ID 12345678901234567890123456

(Yearly) (Formatted No201) error file name When a response file is generated at 10:5:20 on May 5, 2015

ERR_9990_12345678901234567890123456_20150505100520.data

4.2.2 File formats

| Item | Data type | Explanation |
| --- | --- | --- |
| Error Message | 6 half-pitch characters + Up to 128 two-byte characters | Error code + half-width space + error message is output. |
|  | (Variable length) |  |

(Supplementary explanations)

Only one target error is output in one file. The output image of the file is shown below.

Set E1001 scheduling category to four digits.

4.2.3 Error Message

Table 4.3 shows the system of the error codes output to the error file.

Table 4.3 Error code system

| Digit | Description |
| --- | --- |
| 1st digit | Message Level E: Error |
| Second digit | Error 1: Power plant 0: Schedule information distribution system |
| 3rd to 5th digit | Serial number |

Table 4.4 lists the error messages output by this system.

Table 4.4 List of error messages

Error Message

Set E1001 scheduling category to four digits.

E1002 scheduling category is set to a number other than one-byte number.

There is an error in the specification of E1003 scheduling category.

Set E1006 power station ID to 26 digits.

E1007 Power Station ID is set to other than one-byte numbers.

Set E1008 MAC address to 12 digits.

E1009 MAC address is set to a character other than one-byte alphanumeric.

Set half-width alphanumeric characters in E1010 MAC addresses in uppercase characters.

There are no fixed schedules (annual) to be delivered E0001.

There are no fixed schedules (monthly) to be delivered E0002.

The scheduled refresh to be delivered E0003 does not exist.

5 Time synchronization

5.1 Overview of time synchronization

Schedule information distribution system

Power plant

①

Query

②

Response

Time synchronization is performed using NTP(Network Time Protocol) between the scheduling information distribution system and the plant.

Figure 5.1 Overview of Time Synchronization

5.2 Time Synchronization Protocol

Describes the client connection method and NTP server settings.

- Client connection method

Table 5.1 Communication Specifications for Time Synchronization

| Communications protocols | NTP(Network Time Protocol) |
| --- | --- |
| Time synchronization method | Step modes |

- NTP server setting

Table 5. 2 NTP Server Settings

| NTP server | FQDN | Re-ene.kyuden.co.jp |
| --- | --- | --- |
|  | Port | 123 |

5.3 Time Synchronization Timing

Schedule information delivery systems and power plants are synchronized at the timing shown in Table 5.3.

Table 5.3 Time Synchronization Timing

| Synchronization timing | Implementation time zone |
| --- | --- |
| Before initial communication ID authentication (including when equipment is replaced) | Optional |
| When the power supply is started | Optional |
| Periodic renewal (up to once a day) | ※ |
| Other manual execution (error retry, etc.) | Optional |

※ The time zone which can be requested in order to load balance the demand to the schedule information distribution system shall be provided. The time period that can be requested shall be made at the timing of Table 5.4 according to the checksum at the end of the plant ID. If time synchronization fails, retry (up to 5 times) at 1-minute intervals. In the case of another error, the retry is continued after 30 minutes.

Table 5.4 Periodic update timing

| Checksum | Implementation time zone |
| --- | --- |
| 0 | 21:00:00 ～ 21:09:59 |
| 1 | 21:30:00 ～ 21:39:59 |
| 2 | 22:00:00 ～ 22:09:59 |
| 3 | 22:30:00 ～ 22:39:59 |
| 4 | 23:00:00 ～ 23:09:59 |
| 5 | 23:30:00 ～ 23:39:59 |
| 6 | 0:00:00 ～ 0:09:59 |
| 7 | 0:30:00 ～ 0:39:59 |
| 8 | 1:00:00 ～ 1:09:59 |
| 9 | 1:30:00 ～ 1:39:59 |